## Instructions
The provided checklist is designed to assist the user with general installation guidance and pre-inspection quality control.
Refer to manufacturer's installation instructions for product specific information which may supercede the information given here.
See DrJ Best Practices for additional Educational Programs

## Checklist
Revised 2/10/2017
Items to be Checked | Designer | Plan Reviewer | Comments
Code Compliance
NFPA 285 testing is not required under the following three conditions:
Condition #1
One-story building AND
Flame spread index 25 or less AND
Smoke developed index of 450 or less AND
FPIS not more than 4" thick AND
Fire sprinkler system is installed AND
FPIS covered by 0.032" aluminum OR
FPIS covered by 0.0160" corrosion resistant steel
Condition #2
FPIS covered by not less than 1" concrete or masonry AND
No airspace between the FPIS and the concrete/masonry
Condition #3
FPIS covered by not less than 1" concrete or masonry AND
Airspace between the FPIS and the concrete/masonry not more than 1" AND
FPIS flame spread index of 25 or less
Proposed design shall be approved where:
Design meets the intent of the code AND
Design is equivalent to the tested assembly in terms of quality, strength, effectiveness, fire resistance, durability and safety
Research report provided to substantiate claim
Compliance Report
Written by an independent source:
Approved by the building official with proper qualifications for the analysis of the engineering principles of materials and methods
Reference specific NFPA 285 pass test results
Include small-scale testing, if appropriate
Specify all assembly components and constructions
Include opening and flashing details, where required
Alternative meets the intent of the code
Alternative is equivalent to the tested assembly